## Version
Reversion Record
Date | Version | Description | Editor | Auditor
2026-01-12 | V1.0 | 1.标明AIO 二代不适用的点位，接口预留上 | Preh | 红色部分为变更点
2026-02-05 | V1.1 | 1.更新消防相关信号 | Preh | 红色部分为变更点
2026-03-25 | V1.2 | 1.更新液冷相关信号 2.调整功能码配置 | Preh | 红色部分为变更点
2026-04-29 | V1.3 | 1.在原有高压箱铜排温度高故障点位替换成电池插箱铜排温度高故障 | Preh | 红色部分为变更点

## Define
Modbus功能码定义（BMSER使用部分）
代码 | 名称 | 作用
0x03 | 读取保持寄存器 | 在一个或多个保持寄存器中取得当前的二进制值
0x04 | 读取输入寄存器 | 在一个或多个输入寄存器中取得当前的二进制值
0x06 | 配置单寄存器 | 配置一个特定的二进制值到一个单寄存器中
0x10 | 配置多寄存器 | 配置一系列特定的二进制值到一系列多寄存器中
Modbus通讯协议定义
Write：
addr | Fun | Data start reg hi | Data start reg lo | D0 #of regs hi | D0 #of regs lo | Byte count | Value hi | Value lo
地址 | 功能码 | 寄存器起始地址高8位 | 寄存器起始地址低8位 | 寄存器数量高8位 | 寄存器数量低8位 | 字节数 | 数据高8位 | 数据低8位
Write Response:
addr | Fun | Data start reg hi | Data start reg lo | D0 #of regs hi | D0 #of regs lo | CRC16 lo | CRC16 hi
地址 | 功能码 | 寄存器起始地址高8位 | 寄存器起始地址低8位 | 寄存器数量高8位 | 寄存器数量低8位 | 校验低8位 | 校验高8位
Read:
addr | Fun | D0 addr hi | D0 addr lo | D0 #of regs hi | D0 #of regs lo | CRC16 lo | CRC16 hi
地址 | 功能码 | 寄存器起始地址高8位 | 寄存器起始地址低8位 | 寄存器数量高8位 | 寄存器数量低8位 | 校验低8位 | 校验高8位
Read Response
addr | Fun | Byte count | Data hi | Data lo | CRC16 lo | CRC16 hi
地址 | 功能码 | 字节数 | 数据位 | 数据位 | 校验低8位 | 校验高8位
错误响应格式
地址 | 0x80+功能码 | 错误码（1字节） | CRC16（2字节）
错误码 | 01 | 非法的功能码
| 02 | 非法的数据地址
| 03 | 非法的数据长度
| 04 | 数据读写失败
校验码域 CRC16
采用标准Modicon Modbus协议中的16位循环冗余校验码（CRC）算法，生成多项式为X15+X13+1，传输时低8位在前，高8位在后。从报文首字节（即地址域）到CRC码之前的所有报文字节都参与CRC码的计算。 生成CRC校验码的具体流程如下： 1) 预置1个16位的CRC寄存器为0xFFFF（全1）。 2) 把数据帧中的第1个8位字节和CRC寄存器中的低8位进行异或运算，结果存回到CRC寄存器中。 3) 将CRC寄存器右移1位，最高位填0，最低位移出并检测。 4) 如果最低位为0，重复第3步（下一次移位）。 如果最低位为1，将CRC寄存器和生成多项式进行异或运算。 5) 重复第3步和第4步，直到8次移位完成，这样数据帧中的1个字节就处理结束了。 6) 重复第2步到第5步，把数据帧中所有字节就处理完毕。 7) 最终，CRC寄存器中的数值就是所求的16位CRC校验码。
校验码域 CRC16 代码
ModbusTCP
ModbusTCP | MBAP |  |  |  | PDU
说明 | 事务处理标识 | 协议标识 | 长度 | 单元标识符 | modbus内容
长度 | 2字节 | 2字节 | 2字节 | 1字节 | N字节
说明 | 可以理解为报文的序列号，一般每次通信之后就要加1以区别不同的通信数据报文。 | 00 00表示ModbusTCP协议。 | 表示接下来的数据长度，单位为字节。全部的长度-6。 | 设备地址 | 功能码开始，不包含crc。
寄存器数据 | 高字节在前，低字节在后
发送注意 | 只读数据读取周期需在200ms-1000ms之间，一帧最多读取120个连续寄存器的数据，超过120个寄存器时，应分多帧读取
设备地址分配
设备类型 |  | BCU
设备地址范围 |  | 0x01-0x41
设备类型 |  | BCU 动环
设备地址范围 |  | 0x7E +BCU ID
BCU
设备地址 | 0x01-0x41
功能定义 | Rack Signal | Rack Measure | Rack Control | Rack Diag | Rack Detail | Rack_Alarm Parameter Set & Read
modbus地址范围 | 0x0001-0x0200 | 0x0201-0x0400 | 0x0401-0x0800 | 0x0801-0x0B00 | 0x1000-0x6000 | 0x6001-0x7000
支持功能码 | 0x03 0x04 | 0x03 0x04 | 0x03 0x04 0x10 0x06 | 0x03 0x04 | 0x03 0x04 | 0x03 0x04 0x10 0x06
硬件端口配置说明
1. 物理层通讯口以太网； 2. 协议为MODBUS TCP； 3. EMS为主机，BMS为从机； 4. TCP报文头不做处理 5. 默认EMS作为客户端，BMS作为服务器； 6. BMS默认地址为192.168.1.199，端口号502 | RS485通信方式说明： 1、物理层通信方式为RS485; 2、通信协议为ModbusRTU； 3、EMS作为主机，BMS作为从机； 4、BMS默认modbus设备地址为1，2，3，4，5，….； 5、BMS默认波特率为57600；
注：预留或内部db暂不存在的寄存器，其name填写reserve+数字，保证同一张表中name唯一即可

## Rack Signal
Rack Signal -- EMS Read From BMS(BCU)
名称 | Name | Description | 定义 | Definition | Comment | Data origin | Number | Addr | Unit | Attribute | Type | use_number
功能安全告警详细故障 | functional_safety_warn | Functional Safety Warn | 0-正常，1-故障 | 0-Normal, 1-Fault |  | BCU | 1 | 0x0010 |  | R | u16
|  |  | bit12:采样芯片极限故障 | Bit12:functional_safety_warn.sample_chip_fault
严重告警 | extern_critical_alarm | Extern Critical Alarm | 0-正常，1-故障 | 0-Normal, 1-Fault |  | BCU | 1 | 0x0012 |  | R | u16
|  |  | Bit0: 电池簇总电压过高1级 | Bit0: extern_critical_alarm.Rack Vol High
|  |  | Bit1: 电池簇总电压过低1级 | Bit1: extern_critical_alarm.Rack Vol Low
|  |  | Bit2: 单体过压1级 | Bit2:extern_critical_alarm.Cell Vol High
|  |  | Bit3: 充放电单体欠压1级 | Bit3: extern_critical_alarm.Chg dsg cell Vol Low
|  |  | Bit4: 放电过流1级 | Bit4: extern_critical_alarm.DischargeCurrent High
|  |  | Bit5: 充电过流1级 | Bit5: extern_critical_alarm.Charge Current High
|  |  | Bit6: 电池簇电池温度过高1级报警 | Bit6: extern_critical_alarm.system temp High
|  |  | Bit7: 电池簇充电温度过低故障1级 | Bit7: extern_critical_alarm.system chg temp Low
|  |  | Bit10: 绝缘电阻严重故障 | Bit10: extern_critical_alarm.Ins Low
|  |  | Bit12: 电池插箱铜排温度过高1级报警 | Bit12: extern_critical_alarm.Battery Rank Busbar Temp High
|  |  | Bit13: 电池簇压差过大1级 | Bit13: extern_critical_alarm.Cell Vol Diff High
|  |  | Bit14: 电池簇电池温差过大1级 | Bit14: extern_critical_alarm.Cell Temp Diff High
告警 | extern_alarm | Extern Alarm | 0-正常，1-告警 | 0-Normal, 1-alarm |  | BCU | 1 | 0x0013 |  | R | u16
|  |  | Bit0: 电池簇总电压过高2级 | Bit0: extern_alarm.Rack Vol High
|  |  | Bit1: 电池簇总电压过低2级 | Bit1: extern_alarm.Rack Vol Low
|  |  | Bit2: 单体过压2级 | Bit2: extern_alarm.Cell Vol High
|  |  | Bit3: 充放电单体欠压2级 | Bit3: extern_alarm.Chg dsg cell Vol Low
|  |  | Bit4: 放电过流2级 | Bit4: extern_alarm.Discharge Current High
|  |  | Bit5: 充电过流2级 | Bit5: extern_alarm.Charge Current High
|  |  | Bit6: 电池簇电池温度过高2级报警 | Bit6: extern_alarm.system temp High
|  |  | Bit7: 电池簇充电温度过低故障2级 | Bit7: extern_alarm.system chg temp Low
|  |  | Bit10: 绝缘电阻中等故障 | Bit10: extern_alarm.Ins Low
|  |  | Bit12: 电池插箱铜排温度过高2级报警 | Bit12: extern_alarm.Battery Rank Busbar Temp High
|  |  | Bit13: 电池簇压差过大2级 | Bit13: extern_alarm.Cell Vol Diff
|  |  | Bit14: 电池簇电池温差过大2级 | Bit14: extern_alarm.Cell Temp Diff
预警 | extern_warn | Extern Warning | 0-正常，1-预警 | 0-Normal, 1-preAlarm |  | BCU | 1 | 0x0014 |  | R | u16
|  |  | Bit0: 电池簇总电压过高3级 | Bit0: extern_warn.Rack Vol High
|  |  | Bit1: 电池簇总电压过低3级 | Bit1: extern_warn.Rack Vol Low
|  |  | Bit2: 单体过压3级 | Bit2: extern_warn.Cell Vol High
|  |  | Bit3: 充放电单体欠压3级 | Bit3: extern_warn.Chg dsg cell Vol Low
|  |  | Bit4: 放电过流3级 | Bit4: extern_warn.Discharge Current High
|  |  | Bit5: 充电过流3级 | Bit5: extern_warn.Charge Current High
|  |  | Bit6: 电池簇电池温度过高3级报警 | Bit6: extern_warn.system temp High
|  |  | Bit7: 电池簇充电温度过低故障3级 | Bit7: extern_warn.system chg temp Low
|  |  | Bit10: 绝缘电阻轻微故障 | Bit10: extern_warn.Ins Low
|  |  | Bit12: 电池插箱铜排温度过高3级报警 | Bit12: extern_warn.Battery Rank Busbar Temp High
|  |  | Bit13: 电池簇压差过大3级 | Bit13: extern_warn.Cell Vol Diff
|  |  | Bit14: 电池簇电池温差过大3级 | Bit14: extern_warn.Cell Temp Diff
严重告警II | extern_critical_alarm | Extern Critical Alarm | 0-正常，1-故障 | 0-Normal, 1-Fault |  | BCU | 1 | 0x0015 |  | R | u16
|  |  | Bit1: 电池插箱总电压过高1级 | Bit1:extern_critical_alarm2.pack_vol_over_high
|  |  | Bit2: 电池插箱总电压过低1级 | Bit2:extern_critical_alarm2.pack_vol_over_low
|  |  | Bit4: 电池插箱压差过大1级 | Bit4:extern_critical_alarm2.pack_vol_diff_over_high
|  |  | Bit5:电池簇充电功率过高1级 | Bit5:extern_critical_alarm2.chg_power_over_high
|  |  | Bit6:电池簇放电功率过高1级 | Bit6:extern_critical_alarm2.dsg_power_over_high
|  |  | Bit7:SOH过低故障1级 | Bit7:extern_critical_alarm2.Soh_over_low
|  |  | Bit9: 静置单体欠压1级 | Bit9:extern_critical_alarm2.System idle cell low
|  |  | Bit10: 电池簇放电&静置电池温度过低故障1级 | Bit10:extern_critical_alarm2.System dsg and idle temp low
|  |  | Bit11-bit15备用 | Bit9-bit15:extern_critical_alarm2.reserve
告警II | extern_alarm | Extern Alarm | 0-正常，1-告警 | 0-Normal, 1-Alarm |  | BCU | 1 | 0x0016 |  | R | u16
|  |  | Bit1: 电池插箱总电压过高2级 | Bit1:extern_alarm2.pack_vol_over_high
|  |  | Bit2: 电池插箱总电压过低2级 | Bit2:extern_alarm2.pack_vol_over_low
|  |  | Bit4: 电池插箱压差过大2级 | Bit4:extern_alarm2.pack_vol_diff_over_high
|  |  | Bit5:电池簇充电功率过高2级 | Bit5:extern_alarm2.chg_power_over_high
|  |  | Bit6:电池簇放电功率过高2级 | Bit6:extern_alarm2.dsg_power_over_high
|  |  | Bit9: 静置单体欠压2级 | Bit9:extern_alarm2.System idle cell low
|  |  | Bit10: 电池簇放电&静置电池温度过低故障2级 | Bit10:extern_alarm2.System dsg and idle temp low
|  |  | Bit11-bit15备用 | Bit9-bit15:extern_alarm2.reserve
预警II | extern_warn | Extern Warning | 0-正常，1-预警 | 0-Normal, 1-PreAlarm |  | BCU | 1 | 0x0017 |  | R | u16
|  |  | Bit1: 电池插箱总电压过高3级 | Bit1:extern_warn2.pack_vol_over_high
|  |  | Bit2: 电池插箱总电压过低3级 | Bit2:extern_warn2.pack_vol_over_low
|  |  | Bit4: 电池插箱压差过大3级 | Bit4:extern_warn2.pack_vol_diff_over_high
|  |  | Bit5:电池簇充电功率过高3级 | Bit5:extern_warn2.chg_power_over_high
|  |  | Bit6:电池簇放电功率过高3级 | Bit6:extern_warn2.dsg_power_over_high
|  |  | Bit9: 静置单体欠压3级 | Bit9:extern_warn2.System idle cell low
|  |  | Bit10: 电池簇放电&静置电池温度过低故障3级 | Bit10:extern_warn2.System dsg and idle temp low
|  |  | Bit11-bit15备用 | Bit9-bit15:extern_warn2.reserve
预上电阶段 | pre_power_stage | Pre-Powering Stage | 0：待启动；1-2：预充中；3：预充成功；4：预充失败 | 0:idle 1/2:start 3:success 4:failure | 预留，AIO2.0不适用，默认填0 | BCU | 1 | 0x0018 |  | R | u16
系统状态 | BCU_state | BCU State | 0:正常 1:禁充 2:禁放 3:待机 4:停机 | 0:Idle 1:forbid charging 2:forbid Discharging 3: Standby 4: Stop | 当前系统状态 | BCU | 1 | 0x0019 |  | R | u16
心跳帧 | reserve4 | heart beat | 循环计数 1S累加 | inc every second |  | BCU | 1 | 0x001A |  | R
预充失败原因 | pre_chg_fail_reason | Pre-Charging Fail Reason |  | （reserve） | 预留，AIO2.0不适用，默认填0 | BCU | 1 | 0x001C |  | R | u16
充放电状态 | current_state | Current State | 0：静置；1：放电；2：充电 | 0:Idle 1:Discharge 2:Charge |  | BCU | 1 | 0x001D |  | R | u16
充满放空标志 | full_or_empty_flag | Full or Empty Flag | bit0:置1充满;bit1:置1放空 | bit0:1 full;bit1:1 empty |  | BCU | 1 | 0x001E |  | R | u16
主控对外接触器总状态 | BCU_conactor_state | Conactor State | Bit0:正极接触状态(0-断开，1-闭合) | Bit0:BCU_conactor_state.pos_relay | 预留，AIO2.0不适用，默认填0 | BCU | 1 | 0x001F |  | R | u16
|  |  | Bit1:预充接触器状态(0-断开，1-闭合) | Bit1:BCU_conactor_state.pre_relay | 预留，AIO2.0不适用，默认填0
|  |  | Bit2:负极接触器状态(0-断开，1-闭合) | Bit2:BCU_conactor_state.neg_relay | 预留，AIO2.0不适用，默认填0
|  |  | Bit3:隔离开关/断路器反馈状态(0-断开，1-闭合) | Bit3:BCU_conactor_state.isolation_switch
|  |  | Bit4:熔断器开关反馈状态(0-断开，1-闭合) | Bit4:BCU_conactor_state.fuse_switch | 预留，AIO2.0不适用，默认填0
平台预留位置 | reserve5 |  |  |  |  | BCU | 27 | 0x0028-0x003F
热管理状态 | Heat management status | Obtain status based on thermal management strategy | 0x0:关闭状态;0x1:内循环状态;0x2:冷却状态；0x3:加热状态 | 0x0: close state;0x1: Internal circulation state; 0x2: Cooling state; 0x3: Heating status; | 当前热管理状态 | BCU | 1 | 0x0040 |  | R | u16
BMS故障等级 | BMS fault level | BMS fault level | 0x0:正常;0x1:1级报警；0x2:2级报警；0x3:3级报警 | 0x0: Normal; 0x1:1 level alarm; 0x2: Level 2 alarm; 0x3: Level 3 alarm | BMS故障等级 | BCU | 1 | 0x0041 |  | R | u16
主控对外故障报警I | BCU_external_fault_alarm_I | External Alarm Of Master_I | 0-正常，1-故障 | 0-Normal, 1-Fault |  | BCU | 1 | 0x0042 |  | R | u16
|  |  | Bit0:熔断器开路故障 | Bit0: Open circuit fault of fuse | 预留，AIO2.0不适用，默认填0
|  |  | Bit1:菊花链/内部CAN通信故障 | Bit1: Daisy chain/ Inner CAN communication failure
|  |  | Bit2:电流采集故障 | Bit2: Current acquisition fault | 电流传感器通信故障或电流传感器内部故障
|  |  | Bit3:断路器无法断开故障 | Bit3: Circuit breaker unable to disconnect fault
|  |  | Bit4:电芯温度采集电路故障 | Bit4: Cell temperature acquisition circuit malfunction
|  |  | Bit5:高压箱铜排温度采集电路故障 | Bit5: Copper bar temperature acquisition circuit malfunction | 预留，AIO2.0不适用，默认填0
|  |  | Bit6:高压采样故障 | Bit6: High voltage sampling fault
|  |  | Bit7:供电电压过高故障 | Bit7: Power supply voltage too high fault
|  |  | Bit8:供电电压过低故障 | Bit8: Low power supply voltage fault
|  |  | Bit9:电芯电压测量故障 | Bit9: Cell voltage measurement fault
|  |  | Bit10:电芯电压采样线断线故障 | Bit10: Battery voltage sampling line disconnection fault
|  |  | Bit11:电芯温度测量故障 | Bit11: Cell temperature measurement fault
|  |  | Bit12:电流零漂轻微故障 | Bit12: Minor current drift fault
|  |  | Bit13:电流零漂中等故障 | Bit13: Current zero drift moderate fault
|  |  | Bit14:电流零漂严重故障 | Bit14: Severe current zero drift fault
主控对外故障报警II | BCU_external_fault_alarm_II | External Alarm Of Master_II | 0-正常，1-故障 | 0-Normal, 1-Fault |  | BCU | 1 | 0x0043 |  | R | u16
|  |  | Bit0:热失控故障 | Bit0: Thermal runaway fault
|  |  | Bit1:均衡电路故障 | Bit1: Equalization circuit fault
|  |  | Bit2:均衡温度过高故障 | Bit2: Too high equilibrium temperature fault
|  |  | Bit10:BMS初始化异常故障 | Bit10:BCU_external_fault_alarm.BCU_self_check
|  |  | Bit11-bit15备用 | Bit11-bit15:reserve
主控对外故障报警III | BCU_external_fault_alarm_III | External Alarm Of Master_III | 0-正常，1-故障 | 0-Normal, 1-Fault |  | BCU | 1 | 0x0044 |  | R | u16
|  |  | Bit0:与消防系统通信故障 | Bit0: Communication failure with fire protection system
|  |  | Bit1:与液冷系统通信故障 | Bit1: Communication failure with liquid cooling system
|  |  | Bit2:与PCS系统通信故障 | Bit2: Communication failure with PCS system
|  |  | Bit3:与EMS系统通信故障 | Bit3: Communication failure with EMS system
|  |  | Bit6:消防系统一级故障 | Bit6: First level malfunction of fire protection system
|  |  | Bit7:消防系统二级故障 | Bit7: Fire protection system secondary fault
|  |  | Bit8:消防系统三级故障 | Bit8: Level 3 fault of fire protection system
|  |  | Bit9:急停故障 | Bit9: Emergency stop fault
|  |  | Bit10:水浸故障 | Bit10: Water immersion fault
|  |  | Bit11:浪涌故障 | Bit11: Surge fault
|  |  | Bit12:门禁打开故障 | Bit12: Door open fault
|  |  | Bit13:液冷机组停机故障 | Bit13: liquid cooling system stop fault
|  |  | Bit14:液冷机组告警故障 | Bit14: liquid cooling system alarm fault
|  |  | Bit15备用 | Bit15:reserve
项目部门预留位置 | reserve6 | project protocol reseved |  | 无 | 特殊项目可以使用该空间 | BCU | 32 | 0x0045-0x005F |  | R | U16

## Rack Detail
Rack Detail -- EMS Read From BMS(BCU)
名称 | Name | Description | 定义 | Definition | ASWName | Comment | Data origin | Number | Addr | Unit | Attribute | Type | use_number
单体电压 | single_vol_n{512} | Single Vol |  |  | BSMR_uCellVltg_A{} |  | BCU | max len = 512 | 0x1401-0x1600 | mV | R | u16 | 260
预留 | reserve4 |  |  |  |  | 52*5=260 | BCU | 512 | 0x1601-0x1800 | --- | R | u16
电池温度 | bat_temp_n{512} | Temp |  |  | BSMR_tCellTemp_A{} | 28*5=140 | BCU | max len = 512 | 0x1801-0x1A00 | 0.1℃ | R | int16
预留 | reserve5 | [5 empty] | BCU | 768 | 0x1A01-0x1D00 | --- | R | u16
PACK1内高压连接器负NTC | HV Connector neg temp_1 | [5 empty] | BCU | 1 | 0x2203 | 0.1℃ | R | int16 | 连续的20个地址，可以连读后解析
PACK1内MSD右NTC | MSD R temp_1 |  |  |  |  | 跨接铝牌上侧 | BCU | 1 | 0x2204 | 0.1℃ | R | int16
PACK1内MSD左NTC | MSD L temp_1 |  |  |  |  | 跨接铝牌下侧 | BCU | 1 | 0x2205 | 0.1℃ | R | int16
PACK1内高压连接器正NTC | HV Connector pos temp_1 | [5 empty] | BCU | 1 | 0x2206 | 0.1℃ | R | int16
PACK2内高压连接器负NTC | HV Connector neg temp_2 | [5 empty] | BCU | 1 | 0x2207 | 0.1℃ | R | int16
PACK2内MSD右NTC | MSD R temp_2 |  |  |  |  | 跨接铝牌上侧 | BCU | 1 | 0x2208 | 0.1℃ | R | int16
PACK2内MSD左NTC | MSD L temp_2 |  |  |  |  | 跨接铝牌下侧 | BCU | 1 | 0x2209 | 0.1℃ | R | int16
PACK2内高压连接器正NTC | HV Connector pos temp_2 | [5 empty] | BCU | 1 | 0x220A | 0.1℃ | R | int16
PACK3内高压连接器负NTC | HV Connector neg temp_3 | [5 empty] | BCU | 1 | 0x220B | 0.1℃ | R | int16
PACK3内MSD右NTC | MSD R temp_3 |  |  |  |  | 跨接铝牌上侧 | BCU | 1 | 0x220C | 0.1℃ | R | int16
PACK3内MSD左NTC | MSD L temp_3 |  |  |  |  | 跨接铝牌下侧 | BCU | 1 | 0x220D | 0.1℃ | R | int16
PACK3内高压连接器正NTC | HV Connector pos temp_3 | [5 empty] | BCU | 1 | 0x220E | 0.1℃ | R | int16
PACK4内高压连接器负NTC | HV Connector neg temp_4 | [5 empty] | BCU | 1 | 0x220F | 0.1℃ | R | int16
PACK4内MSD右NTC | MSD R temp_4 |  |  |  |  | 跨接铝牌上侧 | BCU | 1 | 0x2210 | 0.1℃ | R | int16
PACK4内MSD左NTC | MSD L temp_4 |  |  |  |  | 跨接铝牌下侧 | BCU | 1 | 0x2211 | 0.1℃ | R | int16
PACK4内高压连接器正NTC | HV Connector pos temp_4 | [5 empty] | BCU | 1 | 0x2212 | 0.1℃ | R | int16
PACK5内高压连接器负NTC | HV Connector neg temp_5 | [5 empty] | BCU | 1 | 0x2213 | 0.1℃ | R | int16
PACK5内MSD右NTC | MSD R temp_5 |  |  |  |  | 跨接铝牌上侧 | BCU | 1 | 0x2214 | 0.1℃ | R | int16
PACK5内MSD左NTC | MSD L temp_5 |  |  |  |  | 跨接铝牌下侧 | BCU | 1 | 0x2215 | 0.1℃ | R | int16
PACK5内高压连接器正NTC | HV Connector pos temp_5 | [5 empty] | BCU | 1 | 0x2216 | 0.1℃ | R | int16
平台预留位置 | reserve14 | [5 empty] | BCU | 256 | 0x3601-0x3700
项目部门预留位置 | reserve15 | project protocol reseved | 无 | 无 |  | 该部分不允许项目部自定义 | BCU | 256 | 0x3701-0x3800 | X | X | X

## Rack Measure
Rack Measure --EMS Read from BMS(BCU)
名称 | Name | Description | 定义 | Definition | Comment | Data origin | Number | Addr | Unit | Attribute | Type | use_number
单体最高电压 | max_cell_vol | Max Cell Vol |  |  |  | BCU | 1 | 0x0210 | mV | R | u16
单体最高电压编号 | max_cell_vol_num | Max Cell Vol Num | #编号 | #number |  | BCU | 1 | 0x0211 |  | R | u16
最高单体所在模组编号 | max_vol_BMU_num | Max Vol BMU Num | #编号 | #number |  | BCU | 1 | 0x0212 |  | R | u16
最高单体在模组中的单体编号 | BMU_max_vol_num | BMU Max Vol Num | #编号 | #number |  | BCU | 1 | 0x0213 |  | R | u16
单体最低电压 | min_cell_vol | Min Cell Vol |  |  |  | BCU | 1 | 0x0214 | mV | R | u16
单体最低电压编号 | min_cell_vol_num | Min Cell Vol Num | #编号 | #number |  | BCU | 1 | 0x0215 |  | R | u16
最低单体所在模组编号 | min_vol_BMU_num | Min Vol BMU Num | #编号 | #number |  | BCU | 1 | 0x0216 |  | R | u16
最低单体在模组中的单体编号 | BMU_min_vol_num | BMU Min Vol Num | #编号 | #number |  | BCU | 1 | 0x0217 |  | R | u16
最高最低单体压差 | max_cell_vol_diff | Max Cell Vol Diff |  |  |  | BCU | 1 | 0x0218 | mV | R | u16
单体平均电压 | ave_cell_vol | Ave Cell Vol |  |  |  | BCU | 1 | 0x0219 | mV | R | u16
电池最高温度 | max_cell_temp | Max Cell Temp |  |  |  | BCU | 1 | 0x021A | 0.1℃ | R | int16
电池最高温度编号 | max_cell_temp_num | MaxCellTemp Num | #编号 | #number |  | BCU | 1 | 0x021B |  | R | u16
最高温度所在从控编号 | max_temp_BMU_num | MaxTempBMU Num | #编号 | #number |  | BCU | 1 | 0x021C |  | R | u16
最高温度在模组中的温度编号 | BMU_max_temp_num | BMU MaxTempNum | #编号 | #number |  | BCU | 1 | 0x021D |  | R | u16
电池最低温度 | min_cell_temp | Min Cell Temp |  |  |  | BCU | 1 | 0x021E | 0.1℃ | R | int16
电池最低温度编号 | min_cell_temp_num | MinCellTemp Num | #编号 | #number |  | BCU | 1 | 0x021F |  | R | u16
最低温度所在模组编号 | min_temp_BMU_num | MinTempBMU Num | #编号 | #number |  | BCU | 1 | 0x0220 |  | R | u16
最低温度在模组中的温度编号 | BMU_min_temp_num | BMU MinTempNum | #编号 | #number |  | BCU | 1 | 0x0221 |  | R | u16
平均温度 | rack_ave_temp | Rack Ave Temp |  |  |  | BCU | 1 | 0x0222 | 0.1℃ | R | int16
最大可接受允许充电电流限值 | max_allowed_chg_cur_limit | Max Allowed Charging Current Limit | 查电池簇电流保护限流表输出 |  |  | BCU | 1 | 0x0225 | 0.1A | R | u16
最大可接受允许放电电流限值 | max_allowed_dchg_cur_limit | Max Allowed Discharging Current Limit | 查电池簇电流保护限流表输出 |  |  | BCU | 1 | 0x0226 | 0.1A | R | u16
显示SOC | display_SOC | Display SOC |  |  |  | BCU | 1 | 0x0227 | ‰ | R | u16
SOH | SOH | SOH |  |  |  | BCU | 1 | 0x0228 | ‰ | R | u16
电池最大温差 | max_bat_temp_diff | Max Bat Temp Diff |  |  | 所有从控电池温度中，最大电池温度和最小电池温度的差值 | BCU | 1 | 0x0229 | 0.1℃ | R | int16
簇内部SOC | rack_inner_SOC | InnerSoc |  |  | 内部SOC值（与db0x0040的值一致） | BCU | 1 | 0x022E | ‰ | R | u16
预充总压 | pre_chg_vol | Precharging Vol |  |  | 预留，AIO2.0不适用，默认填0 | BCU | 1 | 0x022F | 0.1V | R | u16
累计总压 | BMU_total_vol | Total accumulated pressure |  |  |  | BCU | 1 | 0x0230 | 0.1V | R | u16
电池总电压 | total_vol | Total Vol |  |  |  | BCU | 1 | 0x0231 | 0.1V | R | u16
总电流（用于SOC积分或对外显示） | total_cur | Total Cur |  |  | Charge current is negative and discharge is positive. | BCU | 1 | 0x0234 | 0.1A | R | int16
绝缘阻值 | Insulation resistance | Insulation resistance |  |  |  | BCU | 1 | 0x0237 | kΩ | R | u16
正端绝缘阻值 | positive insulation resistance | Positive Insulation |  |  |  | BCU | 1 | 0x0238 | kΩ | R | u16
负端绝缘阻值 | negative insulation resistance | Negative Insulation |  |  |  | BCU | 1 | 0x0239 | kΩ | R | u16
供电采样电压 | supply_sample_vol | Supply Voltage |  |  |  | BCU | 1 | 0x023A | mV | R | u16
铜排温度最高温度 | HV_Box_max_temp | HV Box Max Temp |  |  | 预留，AIO2.0不适用，默认填0 | BCU | 1 | 0x023B | 0.1℃ | R | int16
高压箱熔丝温度1 | HV_box_fuse_temp1 | HV_box_fuse_temp1 | 高压箱熔丝 | High voltage box fuse | 预留，AIO2.0不适用，默认填0 | BCU | 1 | 0x023C | 0.1℃ | R | int16
高压箱OUTPUT温度2 | HV_box_OUTPUT_temp2 | HV_box_OUTPUT_temp2 | 高压箱OUTPUT | High voltage box OUTPUT | 预留，AIO2.0不适用，默认填0 | BCU | 1 | 0x023D | 0.1℃ | R | int16
高压箱铜排温度3 | HV_box_temp3 | HV_box_temp3 | 铜牌温度 | Bronze plate temperature | 预留，AIO2.0不适用，默认填0 | BCU | 1 | 0x023E | 0.1℃ | R | int16
高压箱铜排温度4 | HV_box_temp4 | HV_box_temp4 | 铜牌温度 | Bronze plate temperature | 预留，AIO2.0不适用，默认填0 | BCU | 1 | 0x023F | 0.1℃ | R | int16
当月累计充电电量 | month_accum_chg_energy | Month Charge Energy |  |  |  | BCU | 1 | 0x0246 | kwh | R | u16
当月累计放电电量 | month_accum_dchg_energy | Month Discharge Energy |  |  |  | BCU | 1 | 0x0247 | kwh | R | u16
当年累计充电电量高16位 | year_chg_energy_h16b | Year Charge Energy High 16 Bit |  |  |  | BCU | 1 | 0x0248 | kwh | R | u16
当年累计充电电量低16位 | year_chg_energy_l16b | Year Charge Energy Low 16 Bit |  |  |  | BCU | 1 | 0x0249 | kwh | R | u16
当年累计放电电量高16位 | year_dchg_energy_h16b | Year Charge Energy High 16 Bit |  |  |  | BCU | 1 | 0x024A | kwh | R | u16
当年累计放电电量低16位 | year_dchg_energy_l16b | Year Discharge Energy Low 16 Bit |  |  |  | BCU | 1 | 0x024B | kwh | R | u16
总累计充电容量高16位 | total_chg_capcity_h16bit | Total Charge Capcity High 16 Bit |  |  |  | BCU | 1 | 0x024C | AH | R | u16
总累计充电容量低16 | total_chg_capcity_l16bit | Total Charge Capcity Low 16 Bit |  |  |  | BCU | 1 | 0x024D | AH | R | u16
总累计放电容量高16位 | total_dchg_capcity_h16bit | Total Discharge Capcity High 16 Bit |  |  |  | BCU | 1 | 0x024E | AH | R | u16
总累计放电容量低16位 | total_dchg_capcity_l16bit | Total Discharge Capcity High 16 Bit |  |  |  | BCU | 1 | 0x024F | AH | R | u16
平台预留位置 | reserve6 |  |  |  |  | BCU | 28 | 0x0254-0x026F
最大可接受充电功率 | max_allowed_chg_power | Max Allowed Charging Power | 限流模块输出 |  |  | BCU | 1 | 0x0270 | 0.1kw | R | u16
最大可接受放电功率 | max_allowed_dchg_power | Max Allowed Discharging Power | 限流模块输出 |  |  | BCU | 1 | 0x0271 | 0.1kw | R | u16
电池簇SOE | rack_soe | rack_soe |  |  |  | BCU | 1 | 0x0272 | ‰ | R | u16
从控01均衡执行状态 | Balance execution status from control 01 | Balance execution status from control 01 | 0x0:均衡关闭； 0x1:均衡开启； 注：从控中任意均衡开启则为开启状态 | 0x0: Balanced off; 0x1: Balance enabled; Note: If any balance is enabled from the control center, it is in the enabled state |  | BCU | 1 | 0x0273 |  | R | u16
从控02均衡执行状态 | Balance execution status from control 02 | Balance execution status from control 02 | 0x0:均衡关闭； 0x1:均衡开启； 注：从控中任意均衡开启则为开启状态 | 0x0: Balanced off; 0x1: Balance enabled; Note: If any balance is enabled from the control center, it is in the enabled state |  | BCU | 1 | 0x0274 |  | R | u16
从控03均衡执行状态 | Balance execution status from control 03 | Balance execution status from control 03 | 0x0:均衡关闭； 0x1:均衡开启； 注：从控中任意均衡开启则为开启状态 | 0x0: Balanced off; 0x1: Balance enabled; Note: If any balance is enabled from the control center, it is in the enabled state |  | BCU | 1 | 0x0275 |  | R | u16
从控04均衡执行状态 | Balance execution status from control 04 | Balance execution status from control 04 | 0x0:均衡关闭； 0x1:均衡开启； 注：从控中任意均衡开启则为开启状态 | 0x0: Balanced off; 0x1: Balance enabled; Note: If any balance is enabled from the control center, it is in the enabled state |  | BCU | 1 | 0x0276 |  | R | u16
从控05均衡执行状态 | Balance execution status from control 05 | Balance execution status from control 05 | 0x0:均衡关闭； 0x1:均衡开启； 注：从控中任意均衡开启则为开启状态 | 0x0: Balanced off; 0x1: Balance enabled; Note: If any balance is enabled from the control center, it is in the enabled state |  | BCU | 1 | 0x0277 |  | R | u16
热失控电池柜编号 | Thermal runaway battery cabinet number | Thermal runaway battery cabinet number | #编号 | #number |  | BCU | 1 | 0x027B |  | R | u16
热失控电池柜中电池插箱编号 | Number of battery insertion box in thermal runaway battery cabinet | Number of battery insertion box in thermal runaway battery cabinet | #编号 | #number |  | BCU | 1 | 0x027C |  | R | u16
BMS绝缘检测功能状态 | BMS insulation detection function status | BMS insulation detection function status | 0：关闭（默认） 1：开启 其它：无效 | 0: Close（default） 1: Enable Other: Invalid | 周期信号 | BCU | 1 | 0x027D |  | R | u16
BMS绝缘检测指令响应状态 | BMS insulation detection command response status | BMS insulation detection command response status | 0：开启成功； 1：无法开启； 2：关闭成功； 3：无法关闭。 0xffff:无效值 | 0: Successfully opened; 1: Unable to open; 2: Successfully closed; 3: Unable to close. 0xffff: Invalid value | 事件信号 | BCU | 1 | 0x027E |  | R | u16
BMS人工关闭绝缘功能指令 | BMS manual shutdown insulation function command | BMS manual shutdown insulation function command | 0：未人工强制关闭（默认） 1：人工强制关闭 | 0: Not manually forced to close（default） 1: Manual forced shutdown | 周期信号 | BCU | 1 | 0x027F |  | R | u16
BMS绝缘检测执行状态 | BMS insulation detection execution status | BMS insulation detection execution status | 0：未检测；（默认） 1：周期性检测； 2：单次检测； 3：检测完成。 | 0: Not detected;（default） 1: Periodic testing; 2: Single test; 3: Detection completed. | 周期信号 | BCU | 1 | 0x0280 |  | R | u16
项目部门预留位置 | reserve7 | project protocol reseved | 无 | 无 | 特殊项目可以使用该空间 | BCU | - | 0x027D-0x028F |  | R | U16

## Rack Control
Rack Control -- EMS Write into BMS(BCU)
名称 | Name | Description | 定义 | Definition | Comment | Data origin | Number | Addr | Unit | Attribute | Type | use_number
启动绝缘采样 | start_insulation_sampleing | Start Insulation Sampleing | 1：使能 2：不使能 | 1： Enable 2： Disable | BMS采集绝缘的开关控制。断网时若需要BMS采集绝缘，则使能此功能，若不需要，则不使能（上位机控制） | BCU/EMS | 1 | 0x0401 | --- | R/W | u16
下高压控制 | Upper and lower high pressure control | Upper and lower high pressure control | 写入值定义： 0x01:电池簇下高压 | write value definition: 0x01: High voltage unde the battery cluster | 1、EMS正常情况下不控制下高压，有需求时再控制。正常BMS有故障会自行下高压 | BCU/EMS | 1 | 0x0402 | --- | R/W | u16
主控复位 | BCU_reset | Reset | 0x1-复位；其它:不复位 | 0x1：Reset ; other:No Reset | 写入0x1，可控制进行主控软件复位；写入其他值无效 EMS无特殊情况，不进行主控复位操作，有需要时手动操作 | BCU/EMS | 1 | 0x0403 | --- | R/W | u16
平台预留位置 | reserve1 |  | 无 | 无 |  | BCU | 28 | 0x0405-0x0464 |  | R/W
一键清除异常事件 | clear_all_abnormal_event | clear_all_abnormal_event | 1:触发清除 | 0x1：clear all fault | 写入0x1，可控制进行主控软件故障复归；写入其他值无效 有需求时手动操作 | BCU/EMS | 1 | 0x0465 | --- | R/W | u16
下一次充放电状态 | Next charging and discharging state during idle state | Next charging and discharging state during idle state | 0x1:下一阶段为充电模式 0x2:下一阶段为放电模式 0xff:无效值 | 0x1: The next stage is charging mode 0x2: The next stage is discharge mode 0xff: Invalid value | 该信号要与下一阶段充电时长一起下发给BMS | BCU/EMS | 1 | 0x0466 |  | R/W | u16
下一阶段充电时长 | Next stage charging duration | Next stage charging duration | 0xffff:无效值 | 0xffff: Invalid value | EMS需要定时更新，静置时先更新一次，之后每10min更新一次。若有重新设置，需立即更新 | BCU/EMS | 1 | 0x0469 | 0.1h | R/W | u16
EMS绝缘检测控制指令 | EMS insulation detection control command | EMS insulation detection control command | 0：开启绝缘检测； 1：关闭绝缘检测。 0xffff:无效值 | 0: Enable insulation detection; 1: Turn off insulation testing. 0xffff: Invalid value | 事件信号 EMS绝缘检测控制开关。并网后是否需要BMS采集绝缘，由此开关进行控制 | BCU/EMS | 1 | 0x046A |  | R/W | u16
项目部门预留位置 | reserve2 | project protocol reseved | 无 | 无 | 特殊项目可以使用该空间 | BCU | - | 0x046B-0x0484 |  | R/W | U16
BCU时间高位 | BCU_sync_time_h16b | BCU Sync Time High 16bit | 需定时进行对时写入 | EMS每间隔10min需要进行一次校准 | 主控时间高16位（EMS用unix时间戳对主控时间进行校准） | BCU/EMS | 1 | 0x0900 |  | R/W | u16
BCU时间低位 | BCU_sync_time_l16b | BCU Sync Time Low 16bit | 需定时进行对时写入 | EMS每间隔10min需要进行一次校准 | 主控时间低16位（EMS用unix时间戳对主控时间进行校准） | BCU/EMS | 1 | 0x0901 |  | R/W | u16

## Rack Diag
Rack Diag -- EMS Read From BMS
名称 | Name | Description | 定义 | Definition | Comment | Data origin | Number | Addr | Unit | Attribute | Type | use_number
主控软件项目编号 | BCU_software_project_num | BCU Software Project Num |  | #Num |  | BCU | 1 | 0x0801 | --- | R | u16
主控软件主版本号 | BCU_software_main_version_num | BCU Software Main Version Num |  | #Num（from 1 to 1000） |  | BCU | 1 | 0x0802 | --- | R | u16
主控软件子版本号 | BCU_software_sub_version_num | BCU Software Sub Version Num |  | #Num（from 1 to 1000） |  | BCU | 1 | 0x0803 | --- | R | u16
主控软件修正版本号 | BCU_software_main_revise_num | BCU Software Main Revise Num |  | #Num（from 1 to 1000） |  | BCU | 1 | 0x0804 | --- | R | u16
所有从控的通信故障信息低16位 | BMU_comm_fault_state_l16b | BMU Comm fault state 1 | 1个bit代表一个从控（0：正常；1：异常） | Each bit Represents a Slave，from Slave 1 to 16（0：Normal；1：Fault） |  | BCU | 1 | 0x080D | Hex | R | u16
所有从控的概要故障信息1-16 | BMU_sum_fault_state1 | BMU fault state 1 | 1个bit代表一个从控（采样芯片故障、电压采样故障、电池温度采样故障只置位每一条菊花链最先发生故障的从控） | Each bit Represents a Slave，from Slave 1 to 16（0：Normal；1：Fault） |  | BCU | 1 | 0x0810 | Hex | R | u16
项目部门预留位置(动环数据) | reserve4 | project protocol reseved |  | 无 | 特殊项目可以使用该空间 | BCU | 32 | 0x0A00-0x0BFF |  | R/W | U16
机组外环境温度 | External ambient temp | External ambient temp | Accuracy 精度 0. 1℃ 举例：0x0010 代表1.6℃ |  |  | BCU/EMS | 1 | 0x0A00 |  | R | int16
液冷机组工作模式 | Lcu running mode | Lcu running mode | 0x01：水泵循环； 0x02：制冷模式； 0x03：制热模式； 0x04：自动控制； | 0x01: water pump circulation 0x02: Refrigeration mode 0x03: Heating mode 0x04: System automatic control mode |  | BCU/EMS | 1 | 0x0A01 |  | R | u16
液冷机组出水设定温度 | Lcu water temp setting | Lcu water temp setting | 设置温度 0.1℃ Set the temp. of 0.1℃ 举例：0x0010 代表1.6℃ 控制方式出水控制 |  |  | BCU/EMS | 1 | 0x0A02 | 0.1℃ | R | int16
液冷机组使能开关 | Lcu enable switch | Lcu enable switch | 0x00：关机； 0x01：开机； | 0x00：Off； 0x01：On； |  | BCU/EMS | 1 | 0x0A03 |  | R | u16
水泵运行状态 | Running state of water pump | Running state of water pump | 1 代表运行,0 代表停止 | 1 means in service, 0 means out of service |  | BCU/EMS | 1 | 0x0A04 |  | R | u16
压缩机运行状态 | Running status of #1 compressor | Running status of #1 compressor | 1 代表运行,0 代表停止 | 1 means in service, 0 means out of service |  | BCU/EMS | 1 | 0x0A05 |  | R | u16
电加热运行状态 | Running status of electric heater | Running status of electric heater | 1 代表运行,0 代表停止 | 1 means in service, 0 means out of service |  | BCU/EMS | 1 | 0x0A06 |  | R | u16
冷凝风机运行状态 | Running status of condensate fan | Running status of condensate fan | 1 代表运行,0 代表停止 | 1 means in service, 0 means out of service |  | BCU/EMS | 1 | 0x0A07 |  | R | u16
机组出水温度 | Outlet water temp | Outlet water temp | Accuracy 精度 0. 1℃ 举例：0x0010 代表1.6℃ |  |  | BCU/EMS | 1 | 0x0A08 | 0.1℃ | R | int16
机组回水温度 | Return water temp | Return water temp | Accuracy 精度 0. 1℃ 举例：0x0010 代表1.6℃ |  |  | BCU/EMS | 1 | 0x0A09 | 0.1℃ | R | int16
机组出水压力 | Water outlet pressure | Water outlet pressure | 精度 Accuracy 0.01Bar 举例：0x0010 代表0.16bar |  |  | BCU/EMS | 1 | 0x0A0A | 0.01Bar | R | u16
机组回水压力 | Return water pressure | Return water pressure | 精度 Accuracy 0.01Bar 举例：0x0010 代表0.16bar |  |  | BCU/EMS | 1 | 0x0A0B | 0.01Bar | R | u16
补液水泵状态 | Status of make-up water pump | Status of make-up water pump | 1:开 0:关 | 1: on 0 :off |  | BCU/EMS | 1 | 0x0A0C |  | R | u16
故障告警代码 | Fault alarm code | Fault alarm code | 参见故障代码表 | See fault code sheet |  | BCU/EMS | 1 | 0x0A0D |  | R | u16
故障等级 | Fault Level | Fault Level | 1：停机 2:只报警 | 1:Stop 0:Alarm |  | BCU/EMS | 1 | 0x0A0E |  | R | u16
消防系统预警等级 | Fire system warning level | Fire system warning level | 消防预警等级 0x00：正常状态 0x01：一级报警 0x02：二级报警 0x03：三级报警 | Fire warning level 0x00: Normal state 0x01: First level alarm 0x02: Level 2 alarm 0x03: Level 3 alarm | 不与传感器编码配合使用 Pack 内报警条件： 一级报警： CAN 接收的 BMS 热失控报警； 储能柜体内传感器报警条件： 一级报警： a. 温度大于 70℃； 或 b. 探测到一氧化碳气体报警信号(＞190ppm )； 或 c. 探测到烟雾报警信号( >0.15dB/m)； 二级报警： a. 温度大于 80℃； 或 b. 探测到烟雾(> 0.35dB/m)及一氧化碳气体(＞300ppm )报警信号； 或 c. 探测到温度突变(10℃/10s@>55℃)报警信息； 三级报警： a.温度大于 90℃及烟雾( >0.55dB/m)一氧化碳气体(＞600ppm )报警； 或 b.温度突变(10℃/10s@>55℃)及烟雾( >0.55dB/m)一氧化碳气体(＞ 600ppm )报警； | BCU/EMS | 1 | 0x0A40 |  | R | u16
消防系统设备状态标志 | Fire system equipment status signs | Fire system equipment status signs | bit0:声光报警器启动标志，0：正常 1：启动 bit1:灭火剂容量标志位，0：正常 1：不足 bit2:启停按钮设备启动信号，0：未按下 1：按下 bit3:启停按钮设备停止信号，0：未按下 1：按下 bit4:灭火器状态，0：灭火器未启动 1：灭火器已启动 | Bit0: Sound and light alarm start flag, 0: Normal 1: Start Bit1: Fire extinguishing agent capacity flag, 0: Normal 1: Insufficient Bit2: Start stop button device start signal, 0: not pressed 1: pressed Bit3: Start stop button device stop signal, 0: not pressed 1: pressed Bit4: Fire extinguisher status, 0: Fire extinguisher not activated 1: Fire extinguisher activated | 不与传感器编码配合使用 bit0:一级报警后声光报警器启动，信号值为1；其他情况置0。 bit1:未启动任一灭火器的情况下，检测到瓶口反馈信号线短接置1；其他情况置0。 bit2:检测到启停按钮设备的启动按钮按下置1，该按钮复位后置0。 bit3:检测到启停按钮设备的停止按钮按下置1，该按钮复位后置0。 bit4:灭火器的瓶口阀启动状态，在瓶口阀驱动启动，且检测到反馈信号之后置1；其他情况置0。 | BCU/EMS | 1 | 0x0A41 |  | R | u16
柜内消防系统烟雾浓度数据 | Inside cabinet fire system smoke concentration data | Inside cabinet fire system smoke concentration data | 烟雾浓度，测量范围：0-2.00dB/m 实际值扩大100倍，计算方式：实际烟雾浓度值= 烟雾浓度数据/100 例如：烟雾浓度数据为15时：0.15dB/m | Smoke concentration, measurement range: 0-2.00dB/m Increase the actual value by 100 times, calculation method: actual smoke concentration value=smoke concentration data/100 For example, when the smoke concentration data is 15, it is 0.15 dB/m | 与传感器编码配合使用 代表探测器探测到的烟雾浓度数据 | BCU/EMS | 1 | 0x0A56 |  | R | u16
柜内消防系统温度数据 | Inside cabinet fire system temp data | Inside cabinet fire system temp data | 温度数据，测量温度范围：-40℃～+125℃ 数据偏移量40，计算方式：实际温度值 = 温度数据-40 例如：温度数据为0时：-40℃ 温度数据为40时：0℃ 温度数据为165时：125℃ | Temperature data, measurement temperature range: -40 ℃ to+125 ℃ Data offset of 40, calculation method: actual temperature value=temperature data-40 For example, when the temperature data is 0: -40 ℃ When the temperature data is 40: 0 ℃ When the temperature data is 165: 125 ℃ | 与传感器编码配合使用 代表探测器探测到的温度数据 | BCU/EMS | 1 | 0x0A57 |  | R | u16
柜内消防系统一氧化碳数据 | Inside cabinet fire system carbon monoxide data | Inside cabinet fire system carbon monoxide data | 一氧化碳浓度，测量范围：0-2550ppm 计算方式：实际一氧化碳浓度值= 一氧化碳浓度数据*10 例如：一氧化碳浓度数据为20时：200ppm | Carbon monoxide concentration, measurement range: 0-2550ppm Calculation method: Actual carbon monoxide concentration value=Carbon monoxide concentration data * 10 For example, when the carbon monoxide concentration data is 20, it is 200ppm | 与传感器编码配合使用 代表探测器探测到的一氧化碳浓度数据 | BCU/EMS | 1 | 0x0A58 |  | R | u16
柜内消防系统状态标志 | Inside cabinet fire system status flag | Inside cabinet fire system status flag | bit0:火灾探测器故障标志，0：正常 1：故障 bit1:消防确认BMS热失控报警标志，0：正常 1：报警 bit2:保留； bit3:火灾探测器报警标志，0：正常 1：报警 | Bit0: Fire detector fault flag, 0: Normal 1: Fault Bit1: Fire Confirmation BMS Thermal Runaway Alarm Flag, 0: Normal, 1: Alarm bit2: reserved; Bit3: Fire detector alarm flag, 0: Normal 1: Alarm | 与传感器编码配合使用 Bit0:传感器地址为0x51~0x55时，该信号值为0，传感器地址为0x56时，检测到传感器离线（10s未收到对应传感器报文）后置1，收到传感器报文后 置0。 Bit1: 收到BMS报文中对应Pack有热失控报警，置1。正常状态置0。 传感器地址为0x51~0x55时，该信号分别代表1~5号电池箱热失控报警标 志，传感器地址为0x56时，该信号值为0。 Bit03 传感器地址为0x51~0x55时，该信号值为0，传感器地址为0x56时，检测到传感器数据有报警等级，置1，正常状态置0。 | BCU/EMS | 1 | 0x0A59 |  | R | u16

## Rack_Alarm Parameter Set & Read (hidden)
RACK Alarm Parameter Threshold Set & Read
Register type: Rack参数设置(保持寄存器, 每Rack Modbus地址独立,从2开始,功能码:0x10或0x06); Rack Parameter Settings (Holding Registers Modbus Addr:each rack independent,from 2 Function Code:0x10 or 0x06)
Modbus Addr: 2 to N+1 (N is rack number)
名称 | Name | Description | 定义 | Definition | Comment | Data origin | Number | Addr | Unit | Attribute | Type | use_number
Rack单体过压一级报警门限 | lv1_hi_clu_sinvol_alm | Rack Cell Over Voltage Warning | lv1_hi_clu_sinvol_alm |  |  | BAU, BCU[1] | 1 | 0x6001 | mv | W/R | u16
Rack单体过压一级恢复门限 | lv1_hi_clu_sinvol_alm_reco | Rack Cell Over Voltage Warning Recover | lv1_hi_clu_sinvol_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6002 | mv | W/R | u16
Rack单体欠压一级报警门限 | lv1_low_clu_sinvol_alm | Rack Cell Under Voltage Warning | lv1_low_total_vol_alm |  |  | BAU, BCU[1] | 1 | 0x6003 | mv | W/R | u16
Rack单体欠压一级恢复门限 | lv1_low_clu_sinvol_alm_reco | Rack Cell Under Voltage Warning Recover | lv1_low_clu_sinvol_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6004 | mv | W/R | u16
Rack总电压过压一级报警门限 | lv1_hi_total_vol_alm | Rack System Over Voltage Warning | lv1_hi_total_vol_alm |  |  | BAU, BCU[1] | 1 | 0x6005 | 0.1V | W/R | u16
Rack总电压过压一级恢复门限 | lv1_hi_total_vol_alm_reco | Rack System Over Voltage Warning Recover | lv1_hi_total_vol_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6006 | 0.1V | W/R | u16
Rack总电压欠压一级报警门限 | lv1_low_total_vol_alm | Rack System Under Voltage Warning | lv1_low_total_vol_alm |  |  | BAU, BCU[1] | 1 | 0x6007 | 0.1V | W/R | u16
Rack总电压欠压一级恢复门限 | lv1_low_total_vol_alm_reco | Rack System Under Voltage Warning Recover | lv1_low_total_vol_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6008 | 0.1V | W/R | u16
Rack充电过流一级报警门限 | lv1_chg_cur_hi_alm | Rack Charge Over Current Warning | lv1_chg_cur_hi_alm |  |  | BAU, BCU[1] | 1 | 0x6009 | 0.1A | W/R | u16
Rack充电过流一级恢复门限 | lv1_hi_chg_cur_alm_reco | Rack Charge Over Current Warning Recover | lv1_hi_chg_cur_alm_reco |  |  | BAU, BCU[1] | 1 | 0x600A | 0.1A | W/R | u16
Rack放电过流一级报警门限 | lv1_dchg_cur_hi_alm | Rack Discharge Over Current Warning | lv1_dchg_cur_hi_alm |  |  | BAU, BCU[1] | 1 | 0x600B | 0.1A | W/R | u16
Rack放电过流一级恢复门限 | lv1_hi_dchg_cur_alm_reco | Rack Discharge Over Current Warning Recover | lv1_hi_dchg_cur_alm_reco |  |  | BAU, BCU[1] | 1 | 0x600C | 0.1A | W/R | u16
Rack充电温度过高一级报警门限 | lv1_clu_chg_temp_hi_alm | Rack Charge Over Temp Warning | lv1_clu_chg_temp_hi_alm |  |  | BAU, BCU[1] | 1 | 0x600D | 0.1℃ | W/R | int16
Rack充电温度过高一级恢复门限 | lv1_hi_clu_chg_temp_alm_reco | Rack Charge Over Temp Warning Recover | lv1_hi_clu_chg_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x600E | 0.1℃ | W/R | int16
Rack充电温度过低一级报警门限 | lv1_clu_chg_temp_low_alm | Rack Charge Under Temp Warning | lv1_clu_chg_temp_low_alm |  |  | BAU, BCU[1] | 1 | 0x600F | 0.1℃ | W/R | int16
Rack充电温度过低一级恢复门限 | lv1_low_clu_chg_temp_alm_reco | Rack Charge Under Temp Warning Recover | lv1_low_clu_chg_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6010 | 0.1℃ | W/R | int16
RackSOC过低一级报警门限 | lv1_SOC_low_warn | Rack SOC Lower Warning | lv1_low_SOC_alm |  |  | BAU, BCU[1] | 1 | 0x6011 | - | W/R | u16
RackSOC过低一级恢复门限 | lv1_low_SOC_alm_reco | Rack SOC Lower Warning Recover | lv1_low_SOC_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6012 | - | W/R | u16
Rack极柱温度过高一级报警门限 | lv1_polarity_temp_hi_alm | Rack Pole Over Temp Warning | lv1_polarity_temp_hi_alm |  |  | BAU, BCU[1] | 1 | 0x6013 | 0.1℃ | W/R | int16
Rack极柱温度过高一级恢复门限 | lv1_hi_polarity_temp_alm_reco | Rack Pole Over Temp Warning Recover | lv1_hi_polarity_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6014 | 0.1℃ | W/R | int16
Rack绝缘失效一级报警门限 | lv1_ir_low_warn | Rack Insulation Failure Warning | lv1_low_vol_diff_alm |  |  | BAU, BCU[1] | 1 | 0x6015 | Ω/V | W/R | u16
Rack绝缘失效一级恢复门限 | lv1_low_ir_alm_reco | Rack Insulation Failure Warning Recover | lv1_low_ir_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6016 | Ω/V | W/R | u16
Rack单体压差过高一级报警门限 | lv1_hi_clu_sinvol_diff_alm | Rack Cell Vol Diff Over Big Warning | lv1_hi_clu_sinvol_diff_alm |  |  | BAU, BCU[1] | 1 | 0x6017 | mv | W/R | u16
Rack单体压差过高一级恢复门限 | lv1_hi_clu_sinvol_diff_alm_reco | Rack Cell Vol Diff Over Big Warning Recover | lv1_hi_clu_sinvol_diff_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6018 | mv | W/R | u16
Rack总电压压差过高一级报警门限 | lv1_hi_vol_diff_alm | Rack Total Vol Diff Over Big Warning | lv1_hi_vol_diff_alm |  |  | BAU, BCU[1] | 1 | 0x6019 | 0.1V | W/R | u16
Rack总电压压差过高一级恢复门限 | lv1_hi_tot_vol_diff_alm_reco | Rack Total Vol Diff Over Big Warning Recover | lv1_hi_tot_vol_diff_alm_reco |  |  | BAU, BCU[1] | 1 | 0x601A | 0.1V | W/R | u16
Rack放电过温一级报警门限 | lv1_hi_clu_temp_alm | Rack Discharge Over Temp Warning | lv1_hi_clu_temp_alm |  |  | BAU, BCU[1] | 1 | 0x601B | 0.1℃ | W/R | int16
Rack放电过温一级恢复门限 | lv1_hi_clu_temp_alm_reco | Rack Discharge Over Temp Warning Recover | lv1_hi_clu_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x601C | 0.1℃ | W/R | int16
Rack放电欠温一级报警门限 | lv1_low_clu_temp_alm | Rack Discharge Under Temp Warning | lv1_low_clu_temp_alm |  |  | BAU, BCU[1] | 1 | 0x601D | 0.1℃ | W/R | int16
Rack放电欠温一级恢复门限 | lv1_low_clu_temp_alm_reco | Rack Discharge Under Temp Warning Recover | lv1_low_clu_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x601E | 0.1℃ | W/R | int16
Rack温差过高一级报警门限 | lv1_hi_bat_temp_diff_alm | Rack Bat Temp Diff Over Big Warning | lv1_hi_bat_temp_diff_alm |  |  | BAU, BCU[1] | 1 | 0x601F | 0.1℃ | W/R | u16
Rack温差过高一级恢复门限 | lv1_hi_bat_temp_diff_alm_reco | Rack Bat Temp Diff Over Big Warning Recover | lv1_hi_bat_temp_diff_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6020 | 0.1℃ | W/R | u16
Rack 高压箱连接器温度过高一级报警门限 | lv1_hi_hvbox_temp_alm | Rack HVB Temp High warning | lv1_hi_hvbox_temp_alm |  |  | BAU, BCU[1] | 1 | 0x6021 | 0.1℃ | W/R | u16
Rack 高压箱连接器温度过高一级恢复门限 | lv1_hi_hvbox_temp_alm_reco | Rack HVB Temp High warning Recover | lv1_hi_hvbox_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6022 | 0.1℃ | W/R | u16
Rack单体过压二级报警门限 | lv2_hi_clu_sinvol_alm | Rack Cell Over Voltage Alarm | lv2_hi_clu_sinvol_alm |  |  | BAU, BCU[1] | 1 | 0x6023 | mv | W/R | u16
Rack单体过压二级恢复门限 | lv2_hi_clu_sinvol_alm_reco | Rack Cell Over Voltage Alarm Recover | lv2_hi_clu_sinvol_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6024 | mv | W/R | u16
Rack单体欠压二级报警门限 | lv2_low_clu_sinvol_alm | Rack Cell Under Voltage Alarm | lv2_low_total_vol_alm |  |  | BAU, BCU[1] | 1 | 0x6025 | mv | W/R | u16
Rack单体欠压二级恢复门限 | lv2_low_clu_sinvol_alm_reco | Rack Cell Under Voltage Alarm Recover | lv2_low_clu_sinvol_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6026 | mv | W/R | u16
Rack总电压过压二级报警门限 | lv2_hi_total_vol_alm | Rack System Over Voltage Alarm | lv2_hi_total_vol_alm |  |  | BAU, BCU[1] | 1 | 0x6027 | 0.1V | W/R | u16
Rack总电压过压二级恢复门限 | lv2_hi_total_vol_alm_reco | Rack System Over Voltage Alarm Recover | lv2_hi_total_vol_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6028 | 0.1V | W/R | u16
Rack总电压欠压二级报警门限 | lv2_low_total_vol_alm | Rack System Under Voltage Alarm | lv2_low_total_vol_alm |  |  | BAU, BCU[1] | 1 | 0x6029 | 0.1V | W/R | u16
Rack总电压欠压二级恢复门限 | lv2_low_total_vol_alm_reco | Rack System Under Voltage Alarm Recover | lv2_low_total_vol_alm_reco |  |  | BAU, BCU[1] | 1 | 0x602A | 0.1V | W/R | u16
Rack充电过流二级报警门限 | lv2_chg_cur_hi_alm | Rack Charge Over Current Alarm | lv2_chg_cur_hi_alm |  |  | BAU, BCU[1] | 1 | 0x602B | 0.1A | W/R | u16
Rack充电过流二级恢复门限 | lv2_hi_chg_cur_alm_reco | Rack Charge Over Current Alarm Recover | lv2_hi_chg_cur_alm_reco |  |  | BAU, BCU[1] | 1 | 0x602C | 0.1A | W/R | u16
Rack放电过流二级报警门限 | lv2_dchg_cur_hi_alm | Rack Discharge Over Current Alarm | lv2_dchg_cur_hi_alm |  |  | BAU, BCU[1] | 1 | 0x602D | 0.1A | W/R | u16
Rack放电过流二级恢复门限 | lv2_hi_dchg_cur_alm_reco | Rack Discharge Over Current Alarm Recover | lv2_hi_dchg_cur_alm_reco |  |  | BAU, BCU[1] | 1 | 0x602E | 0.1A | W/R | u16
Rack充电温度过高二级报警门限 | lv2_clu_chg_temp_hi_alm | Rack Charge Over Temp Alarm | lv2_clu_chg_temp_hi_alm |  |  | BAU, BCU[1] | 1 | 0x602F | 0.1℃ | W/R | int16
Rack充电温度过高二级恢复门限 | lv2_hi_clu_chg_temp_alm_reco | Rack Charge Over Temp Alarm Recover | lv2_hi_clu_chg_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6030 | 0.1℃ | W/R | int16
Rack充电温度过低二级报警门限 | lv2_clu_chg_temp_low_alm | Rack Charge Under Temp Alarm | lv2_clu_chg_temp_low_alm |  |  | BAU, BCU[1] | 1 | 0x6031 | 0.1℃ | W/R | int16
Rack充电温度过低二级恢复门限 | lv2_low_clu_chg_temp_alm_reco | Rack Charge Under Temp Alarm Recover | lv2_low_clu_chg_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6032 | 0.1℃ | W/R | int16
RackSOC过低二级报警门限 | lv2_SOC_low_alm | Rack SOC Lower Alarm | lv2_low_SOC_alm |  |  | BAU, BCU[1] | 1 | 0x6033 | 1% | W/R | u16
RackSOC过低二级恢复门限 | lv2_low_SOC_alm_reco | Rack SOC Lower Alarm Recover | lv2_low_SOC_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6034 | 1% | W/R | u16
Rack极柱温度过高二级报警门限 | lv2_polarity_temp_hi_alm | Rack Pole Over Temp Alarm | lv2_polarity_temp_hi_alm |  |  | BAU, BCU[1] | 1 | 0x6035 | 0.1℃ | W/R | int16
Rack极柱温度过高二级恢复门限 | lv2_hi_polarity_temp_alm_reco | Rack Pole Over Temp Alarm Recover | lv2_hi_polarity_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6036 | 0.1℃ | W/R | int16
Rack绝缘失效二级报警门限 | lv2_ir_low_alm | Rack Insulation Failure Alarm | lv2_low_vol_diff_alm |  |  | BAU, BCU[1] | 1 | 0x6037 | Ω/V | W/R | u16
Rack绝缘失效二级恢复门限 | lv2_low_ir_alm_reco | Rack Insulation Failure Alarm Recover | lv2_low_ir_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6038 | Ω/V | W/R | u16
Rack单体压差过高二级报警门限 | lv2_hi_clu_sinvol_diff_alm | Rack Cell Vol Diff Over Big Alarm | lv2_hi_clu_sinvol_diff_alm |  |  | BAU, BCU[1] | 1 | 0x6039 | mv | W/R | u16
Rack单体压差过高二级恢复门限 | lv2_hi_clu_sinvol_diff_alm_reco | Rack Cell Vol Diff Over Big Alarm Recover | lv2_hi_clu_sinvol_diff_alm_reco |  |  | BAU, BCU[1] | 1 | 0x603A | mv | W/R | u16
Rack总电压压差过高二级报警门限 | lv2_hi_vol_diff_alm | Rack Total Vol Diff Over Big Alarm | lv2_hi_vol_diff_alm |  |  | BAU, BCU[1] | 1 | 0x603B | 0.1V | W/R | u16
Rack总电压压差过高二级恢复门限 | lv2_hi_tot_vol_diff_alm_reco | Rack Total Vol Diff Over Big Alarm Recover | lv2_hi_tot_vol_diff_alm_reco |  |  | BAU, BCU[1] | 1 | 0x603C | 0.1V | W/R | u16
Rack放电过温二级报警门限 | lv2_hi_clu_temp_alm | Rack Discharge Over Temp Alarm | lv2_hi_clu_temp_alm |  |  | BAU, BCU[1] | 1 | 0x603D | 0.1℃ | W/R | int16
Rack放电过温二级恢复门限 | lv2_hi_clu_temp_alm_reco | Rack Discharge Over Temp Alarm Recover | lv2_hi_clu_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x603E | 0.1℃ | W/R | int16
Rack放电欠温二级报警门限 | lv2_low_clu_temp_alm | Rack Discharge Under Temp Alarm | lv2_low_clu_temp_alm |  |  | BAU, BCU[1] | 1 | 0x603F | 0.1℃ | W/R | int16
Rack放电欠温二级恢复门限 | lv2_low_clu_temp_alm_reco | Rack Discharge Under Temp Alarm Recover | lv2_low_clu_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6040 | 0.1℃ | W/R | int16
Rack温差过高二级报警门限 | lv2_hi_bat_temp_diff_alm | Rack Bat Temp Diff Over Big Alarm | lv2_hi_bat_temp_diff_alm |  |  | BAU, BCU[1] | 1 | 0x6041 | 0.1℃ | W/R | u16
Rack温差过高二级恢复门限 | lv2_hi_bat_temp_diff_alm_reco | Rack Bat Temp Diff Over Big Alarm Recover | lv2_hi_bat_temp_diff_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6042 | 0.1℃ | W/R | u16
Rack 高压箱连接器温度过高二级报警门限 | lv2_hi_hvbox_temp_alm | Rack HVB Temp High Alarm | lv2_hi_hvbox_temp_alm |  |  | BAU, BCU[1] | 1 | 0x6043 | 0.1℃ | W/R | u16
Rack 高压箱连接器温度过高二级恢复门限 | lv2_hi_hvbox_temp_alm_reco | Rack HVB Temp High Alarm Recover | lv2_hi_hvbox_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6044 | 0.1℃ | W/R | u16
Rack单体过压三级报警门限 | lv3_hi_clu_sinvol_alm | Rack Cell Over Voltage Critical Alarm | lv3_hi_clu_sinvol_alm |  |  | BAU, BCU[1] | 1 | 0x6045 | mv | W/R | u16
Rack单体过压三级恢复门限 | lv3_hi_clu_sinvol_alm_reco | Rack Cell Over Voltage Critical Alarm Recover | lv3_hi_clu_sinvol_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6046 | mv | W/R | u16
Rack单体欠压三级报警门限 | lv3_low_clu_sinvol_alm | Rack Cell Under Voltage Critical Alarm | lv3_low_total_vol_alm |  |  | BAU, BCU[1] | 1 | 0x6047 | mv | W/R | u16
Rack单体欠压三级恢复门限 | lv3_low_clu_sinvol_alm_reco | Rack Cell Under Voltage Critical Alarm Recover | lv3_low_clu_sinvol_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6048 | mv | W/R | u16
Rack总电压过压三级报警门限 | lv3_hi_total_vol_alm | Rack System Over Voltage Critical Alarm | lv3_hi_total_vol_alm |  |  | BAU, BCU[1] | 1 | 0x6049 | 0.1V | W/R | u16
Rack总电压过压三级恢复门限 | lv3_hi_total_vol_alm_reco | Rack System Over Voltage Critical Alarm Recover | lv3_hi_total_vol_alm_reco |  |  | BAU, BCU[1] | 1 | 0x604A | 0.1V | W/R | u16
Rack总电压欠压三级报警门限 | lv3_low_total_vol_alm | Rack System Under Voltage Critical Alarm | lv3_low_total_vol_alm |  |  | BAU, BCU[1] | 1 | 0x604B | 0.1V | W/R | u16
Rack总电压欠压三级恢复门限 | lv3_low_total_vol_alm_reco | Rack System Under Voltage Critical Alarm Recover | lv3_low_total_vol_alm_reco |  |  | BAU, BCU[1] | 1 | 0x604C | 0.1V | W/R | u16
Rack充电过流三级报警门限 | lv3_chg_cur_hi_alm | Rack Charge Over Current Critical Alarm | lv3_chg_cur_hi_alm |  |  | BAU, BCU[1] | 1 | 0x604D | 0.1A | W/R | u16
Rack充电过流三级恢复门限 | lv3_hi_chg_cur_alm_reco | Rack Charge Over Current Critical Alarm Recover | lv3_hi_chg_cur_alm_reco |  |  | BAU, BCU[1] | 1 | 0x604E | 0.1A | W/R | u16
Rack放电过流三级报警门限 | lv3_dchg_cur_hi_alm | Rack Discharge Over Current Critical Alarm | lv3_dchg_cur_hi_alm |  |  | BAU, BCU[1] | 1 | 0x604F | 0.1A | W/R | u16
Rack放电过流三级恢复门限 | lv3_hi_dchg_cur_alm_reco | Rack Discharge Over Current Critical Alarm Recover | lv3_hi_dchg_cur_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6050 | 0.1A | W/R | u16
Rack充电温度过高三级报警门限 | lv3_clu_chg_temp_hi_alm | Rack Charge Over Temp Critical Alarm | lv3_clu_chg_temp_hi_alm |  |  | BAU, BCU[1] | 1 | 0x6051 | 0.1℃ | W/R | int16
Rack充电温度过高三级恢复门限 | lv3_hi_clu_chg_temp_alm_reco | Rack Charge Over Temp Critical Alarm Recover | lv3_hi_clu_chg_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6052 | 0.1℃ | W/R | int16
Rack充电温度过低三级报警门限 | lv3_clu_chg_temp_low_alm | Rack Charge Under Temp Critical Alarm | lv3_clu_chg_temp_low_alm |  |  | BAU, BCU[1] | 1 | 0x6053 | 0.1℃ | W/R | int16
Rack充电温度过低三级恢复门限 | lv3_low_clu_chg_temp_alm_reco | Rack Charge Under Temp Critical Alarm Recover | lv3_low_clu_chg_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6054 | 0.1℃ | W/R | int16
RackSOC过低三级报警门限 | lv3_SOC_low_alm | Rack SOC Lower Critical Alarm | lv3_low_SOC_alm |  |  | BAU, BCU[1] | 1 | 0x6055 | % | W/R | u16
RackSOC过低三级恢复门限 | lv3_low_SOC_alm_reco | Rack SOC Lower Critical Alarm Recover | lv3_low_SOC_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6056 | % | W/R | u16
Rack极柱温度过高三级报警门限 | lv3_polarity_temp_hi_alm | Rack Pole Over Temp Critical Alarm | lv3_polarity_temp_hi_alm |  |  | BAU, BCU[1] | 1 | 0x6057 | 0.1℃ | W/R | int16
Rack极柱温度过高三级恢复门限 | lv3_hi_polarity_temp_alm_reco | Rack Pole Over Temp Critical Alarm Recover | lv3_hi_polarity_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6058 | 0.1℃ | W/R | int16
Rack绝缘失效三级报警门限 | lv3_ir_low_alm | Rack Insulation Failure Critical Alarm | lv3_low_vol_diff_alm |  |  | BAU, BCU[1] | 1 | 0x6059 | Ω/V | W/R | u16
Rack绝缘失效三级恢复门限 | lv3_low_ir_alm_reco | Rack Insulation Failure Critical Alarm Recover | lv3_low_ir_alm_reco |  |  | BAU, BCU[1] | 1 | 0x605A | Ω/V | W/R | u16
Rack单体压差过高三级报警门限 | lv3_hi_clu_sinvol_diff_alm | Rack Cell Vol Diff Over Big Critical Alarm | lv3_hi_clu_sinvol_diff_alm |  |  | BAU, BCU[1] | 1 | 0x605B | mv | W/R | u16
Rack单体压差过高三级恢复门限 | lv3_hi_clu_sinvol_diff_alm_reco | Rack Cell Vol Diff Over Big Critical Alarm Recover | lv3_hi_clu_sinvol_diff_alm_reco |  |  | BAU, BCU[1] | 1 | 0x605C | mv | W/R | int16
Rack总电压压差过高三级报警门限 | lv3_hi_vol_diff_alm | Rack Total Vol Diff Over Big Critical Alarm | lv3_hi_vol_diff_alm |  |  | BAU, BCU[1] | 1 | 0x605D | 0.1V | W/R | int16
Rack总电压压差过高三级恢复门限 | lv3_hi_tot_vol_diff_alm_reco | Rack Total Vol Diff Over Big Critical Alarm Recover | lv3_hi_tot_vol_diff_alm_reco |  |  | BAU, BCU[1] | 1 | 0x605E | 0.1V | W/R | int16
Rack放电过温三级报警门限 | lv3_hi_clu_temp_alm | Rack Discharge Over Temp Critical Alarm | lv3_hi_clu_temp_alm |  |  | BAU, BCU[1] | 1 | 0x605F | 0.1℃ | W/R | int16
Rack放电过温三级恢复门限 | lv3_hi_clu_temp_alm_reco | Rack Discharge Over Temp Critical Alarm Recover | lv3_hi_clu_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6060 | 0.1℃ | W/R | u16
Rack放电欠温三级报警门限 | lv3_low_clu_temp_alm | Rack Discharge Under Temp Critical Alarm | lv3_low_clu_temp_alm |  |  | BAU, BCU[1] | 1 | 0x6061 | 0.1℃ | W/R | u16
Rack放电欠温三级恢复门限 | lv3_low_clu_temp_alm_reco | Rack Discharge Under Temp Critical Alarm Recover | v3_low_clu_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6062 | 0.1℃ | W/R | u16
Rack温差过高三级报警门限 | lv3_hi_bat_temp_diff_alm | Rack Bat Temp Diff Over Big Critical Alarm | lv3_hi_bat_temp_diff_alm |  |  | BAU, BCU[1] | 1 | 0x6063 | 0.1℃ | W/R | u16
Rack温差过高三级恢复门限 | lv3_hi_bat_temp_diff_alm_reco | Rack Bat Temp Diff Over Big Critical Alarm Recover | lv3_hi_bat_temp_diff_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6064 | 0.1℃ | W/R | u16
Rack 高压箱连接器温度过高三级报警门限 | lv3_hi_hvbox_temp_alm | Rack HVB Temp High Critical Alarm | lv3_hi_hvbox_temp_alm |  |  | BAU, BCU[1] | 1 | 0x6065 | 0.1℃ | W/R | u16
Rack 高压箱连接器温度过高三级恢复门限 | lv3_hi_hvbox_temp_alm_reco | Rack HVB Temp High Critical Alarm Recover | lv3_hi_hvbox_temp_alm_reco |  |  | BAU, BCU[1] | 1 | 0x6066 | 0.1℃ | W/R | u16
Rack 模组压差过高告警三级阈值 | lv3_module_vol_differ_hi_alm_throld |  | lv3_module_vol_ differ_hi_alm_throld |  |  | BAU, BCU[1] |  | 0x6067 | 0.1V | W/R | u16
Rack 模组压差过高告警二级阈值 | lv2_module_vol_differ_hi_alm_throld |  | lv2_module_vol_ differ_hi_alm_throld |  |  | BAU, BCU[1] |  | 0x6068 | 0.1V | W/R | u16
Rack 模组压差过高告警一级阈值 | lv1_module_vol_differ_hi_alm_throld |  | lv1_module_vol_ differ_hi_alm_throld |  |  | BAU, BCU[1] |  | 0x6069 | 0.1V | W/R | u16
Rack 模组压差过高告警三级恢复阈值 | lv3_module_vol_differ_hi_alm_reco |  | lv3_module_vol_ differ_hi_alm_reco |  |  | BAU, BCU[1] |  | 0x606A | 0.1V | W/R | u16
Rack 模组压差过高告警二级恢复阈值 | lv2_module_vol_differ_hi_alm_reco |  | lv2_module_vol_ differ_hi_alm_reco |  |  | BAU, BCU[1] |  | 0x606B | 0.1V | W/R | u16
Rack 模组压差过高告警一级恢复阈值 | lv1_module_vol_differ_hi_alm_reco |  | lv1_module_vol_ differ_hi_alm_reco |  |  | BAU, BCU[1] |  | 0x606C | 0.1V | W/R | u16